## Slide 1: Hospital Department Renovation Unit Costs
Colby Vetter
Senior Estimator
JE Dunn Construction

## Slide 2: Objectives:
  Construction Cost Inclusions and Exclusions
  Hospital Department Unit Cost Range
  Factors For Variance in Unit Costs

## Slide 3
Unit Cost Range
  Size of Project – “Economy of Scale”
  Phased
    Relocations
    Extended General Conditions – 4%-12% of Cost
  Cost Escalations
    5%-7% Per Year, Currently – Applied Quarterly
  Project Location – Urban vs Rural
    Proximity to Contractor Pool
  Additional Parameters
    Off Hours Requirements
    Neighboring Departments
    Elevated vs SOG

## Slide 4: Unit Cost Range
Construction Contingencies
  Normally Not Included in Hard Bid Contract
    Applied to Competitive GMP Based off Early Docs
  Percentage Dependent on Design
    Level of Detail
    Detail Increases, Contingency Decreases
    10%-12% At Early Stages, 2%-3% at full design
Not Uncommon for Owner to Carry Separate Contingency for Unknowns or Scope

## Slide 5: Unit Cost Range
Typically Included in Construction Costs:
  General Conditions
    Temporary Measures
  Permits
  Necessary Bonds
  Insurance
  Construction Costs
    Infectious Control
    Demolition
  Contractor Contingency
  Fees

## Slide 6: Unit Cost Range
Levels of Renovation
  Light
    Finishes
  Medium
    Some reconfiguration
  Heavy
    Gut & Remodel

## Slide 7: Unit Cost Range
Levels of Renovation
  Light
    Finishes
  Medium
    Some Reconfiguration
  HEAVY
    Gut & Remodel

## Slide 8: Departments
Entry & Main Lobby - $120 – $170 / SF
  Higher Level of Finishes
    Tile, Carpet, Walk-Off Mat
    Architectural Features
      Ceiling Soffits and Light Coves
      Donor Wall
      Centerpiece – Fireplace or Waterfall
    Millwork – Nourishment Station, Kiosks, Etc…
    Reception Desks, Check-In Station
    Relatively Open Space
    Low Voltage – V&D, Speaker System
  Entry – Aluminum Entrance or Revolving Doors
  Gift Shop
    Interior Glazed Wall – Wood or Aluminum
    Millwork

## Slide 9: Departments
Administration & Offices - $100 - $135 / SF
  High Density of Walls / Doorways
  Level of Finish
    Carpet & Paint
  Lower Level of Millwork & Casework
  Conference Spaces – Can Have Higher Level of Finish
    Millwork
    Projection Screens
    Video Conference Capabilities
  Power & Voice & Data
  Controlled Access - $2k - $3k / Door

## Slide 10: Departments
Waiting Room Spaces - $95 - $125 / SF
  Level of Finishes
    Similar to Lobby
  Support Spaces – Nourishment, Quiet Rooms
  Millwork & Casework
  Controlled Access
  Sound System & Public Address

## Slide 11: Departments
Exam & Clinic Spaces - $145- $180 / SF
  Density of Partitions – Sound Control
  Level of Finish
    Sheet Vinyl vs Carpet & VCT
  Level of Casework – Typ. Rooms, Nurse Stations
    Extent of Blocking & Backing
  Specialties – Wall Protection, Curtain Track, B.A.
  Toilet Count – Dependent on Clinic Type
  V&D & Equipment Power Requirements
  Special Systems – Nurse Call, Access Control
  Configuration

## Slide 12: Exam Room Double Door Configuration

## Slide 13: Departments
Emergency Department - $255- $315 / SF
  Specialty Doors
    Sliding Entry
    Telescoping ED - $4,500-$5,000/ Set
    Auto Operators - $2,500-$3,000/Set
  Cleanable Surfaces
    Hardened Ceiling – GWB vs ATC
    Epoxy Paint, Sheet Vinyl/Epoxy Floors
    Specialties – Wall Protection/B.A./CCT/Rails
  Decontamination – Shower & Collector
  Ceiling-Mounted Equipment – Bracing
  Headwalls & Med Gas
  Phased Construction - Must Remain Operational
  Temporary Entry/Locations
  Emergency Power

## Slide 14: Departments
Patient Rooms - $210 - $268 / SF
  Level of Finish – Med-Surg to ICU rooms
    Sheet Vinyl Flooring at Rooms
    Core Areas
  Millwork
    Headwalls & Footwalls
    Storage Cabinets
    Countertops & Workspaces
    Solid Surface Material (SSM) Tops
    Nurse Stations & Support Area Casework
  Specialties – B.A., Wall Protection, Rails, Patient Lifts (Support)
  Pneumatic Tube Stations
  Restrooms
    Double Bed to Single Bed Rooms
    ICU May or May Not Include a Restroom
    Underfloor Piping
  Medical Gas Outlets
  Special Systems & Emergency Power
    Infant Alarm Systems at Neonatal Floors.
    Controlled Access, Nurse Call, V&D

## Slide 15: Departments
Behavioral Units - $230- $260 / SF
  “Hardened” Space – Patient/Staff Protection
    Reinforced Partitions-Plywood, Fiberglass
    Shatterproof Barrier at Exterior Windows
    Vandal-Proof Specialties
    Hard Ceilings – Drywall
  Monitoring Systems
  Specialty Access Door Systems – Wicket Door System
  Controlled Access
  Temporary Facilities
    Hardened Temporary Walls
    Phased
    Additional Construction Manpower – Security Watch

## Slide 16: Behavioral Unit “Wicket” Door

## Slide 17: Departments
Surgery Department - $260 – $360 / SF
  Finishes
    Sterile Atmosphere
      Flooring – Epoxy or Rubber Floor
      Epoxy Painted Walls
      Hard Ceilings
  Bracing for Ceiling-Mounted Equipment/Booms
  Auto Door Operators
  Specialties – Wall Protection
  Specialized HVAC – Hepa, S.S. Duct
  Independent Unit for Surgery Area – Additional Cooling Loads
  Medical Gases
  Plumbing Fixtures – Scrub Sinks (Owner or GC Supplied?)
  Emergency Power
  Support Spaces
    Lounges & Locker Rooms
    Central Sterile

## Slide 18: Departments
Pre & Post Op - $230 – $280 / SF
  Level of Finish
    Sheet Vinyl, Wall Finish
    Soffits
  Compartmentalized vs Open - Bays
  Casework – Storage & Nurse Stations
  Specialties – Wall Protection, B.A., CCT
  Medical Gases
  Emergency Power Requirements
  Special Systems – Nurse Call, A/V

## Slide 19: Departments
Lab Space & Pharmacy - $215 – $265 / SF
  Generally, Large Open Spaces
  Level of Finishes Varies – Standard to Sterile
  Laboratory Casework – By Owner or GC
  Pharmacy Casework – Split Retail Counters vs. Shelving
  Laboratory Equipment – By Owner
    Include MEP Connections
  Coordination of OFOI Equip
  Fume Hoods – Exhaust
  Pneumatic Tube Stations.
  Controlled Access
  Emergency Power – Lab Equipment

## Slide 20: Departments
Imaging - $235 - $310 / SF
  MRI, CT, PET, Linear Accelerator
  Shielding
    Lead-Lined Drywall - $10 - $12 / SF Premium
    Copper Shielding - $60k - $75k for typical room config.
    Concrete or Lead Brick (Linear Accelerator) 3’-6’ thick
      Vault - $700-1,000 / SF
      Envelope – Maze door - $50K.
  Smaller Square Footages
  High Level of Electrical Rough-In – Control Cabling
  Equipment Access to Space – Level of Complexity
  Coordination of Staging & Installation of OFOI Equipment
  Higher Cooling Load – MRI: Added Chiller. By Whom?
  Location of Power Source

## Slide 21: Departments
Servery & Dining - $120 - $200 / SF
  Kitchen Equipment Can Be Included, Or By Owner
    Equipment: $70 – $140 / Square Foot of Kitchen.
    Servery vs. Food Prep
  Level of Finish
    Floor Finishes – VCT to Tile
    Wall Finishes – Paint to VWC, FRP, Stainless Steel
    Millwork – Trim & Paneling
    Dining Casework – Owner’s Vendor
  Phasing – Renovated in Space, Operational.
  High MEP Requirements
    Sinks & Drains
    Equipment Hook-Ups
    Hoods & Ansul Systems

## Slide 22: Departments
Gang Restrooms - $40,000 - $60,000 / Each
  A.D.A. Upgrades
  Level of Finish
    Tile
  Specialties
    Compartments
    Bath Accessories
  Ceilings – GWB vs ATC
  Mechanical
    Fixture Quantity - $2,500-$3,500/Fixture
    Below-Floor Rough-In – Elevated vs SOG
    Bariatric Fixtures
  Light Fixtures – Decorative
  Small Area – Unable to Stack Trades

## Slide 23: Structure
Building Envelope
Single vs Multi Story
  Structure – Steel, Concrete, Wood
  Foundation Type – Shallow vs. Deep
  Skin – Brick, Glazing, Metal Panel
  Vertical Transportation
  MEP Systems – Independent vs CUP
  Sitework
    Earthwork – Balanced Site
    Retaining Walls
    Landscaping
    Paving & Parking
  Design for Future Expansion

## Slide 24: Not Generally Included in Cost
Design Fees
  Architectural – 6%-12% of Construction Costs
    Civil, Structural, & MEP
  FF&E – Furniture, Fixtures, & Equipment
    Laboratory, Kitchen Equipment
    Medical Equipment – Booms, Gurneys, Sharp’s, etc…
    Technology - Phone & Computer Equipment
      Data Cabling
    Furniture & Systems Furniture
    Artwork
  Signage – Interior & Exterior
  Testing & Inspections
  MEP Commissioning
  Asbestos Abatement or Mold Mitigation

## Slide 25: Questions?

## Slide 26
THANK YOU FOR YOUR TIME!
Enjoy the Conference!